## Slide 1: Brick: Towards a Unified Metadata Schema For Buildings
http://brickschema.org/

## Slide 2: A Vision for “Smart Buildings”
Infrastructure: Sensors Equipment
Thermostat
HVAC
Lighting
Motion Sensor
Smoke Detector
Fire Safety
Management Services
Data Storage
Search
Privacy
Access Control
APIs
Monitoring
Applications
Occupant Interaction
Predictive Control
Fault Detection
NILM
Demand Response
Occupancy Models
Buildings
Office
Hospital
Shopping Mall
Factory
Home
Research Lab

## Slide 3: Data From Buildings Faces Significant Challenges in Integration
Apps need to understand building metadata
  Location of sensors and equipment
  How equipment connect with each other
  Configuration parameters of control systems
But metadata not consistent or machine readable
  E.g. “Temperature” -> “Temp”, “Temporary” -> “Temp”
Metadata varies with building, vendor, type of system
Temperature sensor as an example
  What? -> air, water
  Where? -> room, exhaust, refrigerator
  How is it used? -> control system, fault
Notes: - Every building has thousands of data points, each of which come from various sensors, equipment
- Metadata for these data points are inconsistent, not machine readable and varies with vendor and usage culture
- Infrastructure configuration varies widely across different types of buildings, weather conditions and vendor
- Illustrate with examples

## Slide 4: Metadata For An Existing Building
Source: EBU3B building at UCSD, built in 2004. Word cloud limited to 200 most frequent words

## Slide 5: We Need a Metadata Schema
Metadata Schema
Infrastructure: Sensors Equipment
Thermostat
HVAC
Lighting
Motion Sensor
Smoke Detector
Fire Safety
Management
Data Storage
Search
Privacy
Access Control
APIs
Monitoring
Applications
Occupant Interaction
Predictive Control
Fault Detection
NILM
Demand Response
Occupancy Models
Buildings
Office
Hospital
Shopping Mall
Factory
Home
Apartment

## Slide 6: Existing Schema Are Inadequate
 | BIM/IFC |  | 
Domain | Construction |  | 
Coverage | Architecture, Mechanical, Electrical Design |  | 
Data Model | EXPRESS |  | 
Limitation | Lack of sensors, equipment |  | 

## Slide 7: Existing Schema Are Inadequate
 | BIM/IFC | SAREF, SSN | 
Domain | Construction | Smart Appliances, Sensor Networks | 
Coverage | Architecture, Mechanical, Electrical Design | Location, Appliance, Sensors | 
Data Model | EXPRESS | Semantic Ontology | 
Limitation | Lack of sensors, equipment | Limited vocabulary | 

## Slide 8: Existing Schema Are Inadequate
 | BIM/IFC | SAREF, SSN | Haystack
Domain | Construction | Smart Appliances, Sensor Networks | Building Management
Coverage | Architecture, Mechanical, Electrical Design | Location, Appliance, Sensors | HVAC, Lighting, Weather, Sensors, Points
Data Model | EXPRESS | Semantic Ontology | Tags
Limitation | Lack of sensors, equipment | Limited vocabulary | Inadequate tooling, limited relationships

## Slide 9: Existing Schema Are Inadequate
Chart: Coverage and Expressiveness in Existing Schema
| BIM/IFC | SSN | Haystack
Coverage | 29 | 11 | 54
Application Requirements | 86 | 41 | 77
Bhattacharya, Arka, Joern Ploennigs, and David Culler. "Short Paper: Analyzing Metadata Schemas for Buildings: The Good, the Bad, and the Ugly." BuildSys, 2015.

## Slide 10: Collaborative Solution to a Common Problem
BuildSys’15
Limitations of existing schema
Feb ‘16
Collaboration initiation
May ‘16
Informal Workshop at Berkeley
Jun ‘16
BuildSys Deadline
BuildSys ‘16
Open Source Release & Demo

## Slide 11
Rajesh Gupta, UCSD
Mikkel Kjaergaard, SDU
Mani Srivastava, UCLA
Kamin Whitehouse, UVA
David Culler, UC Berkeley
Jason Koh, UCSD
Jingkun Gao, CMU
Joern Ploennigs, IBM
Yuvraj Agarwal, CMU
Mario Berges, CMU
Joshua Gluck, CMU
Dezhi Hong, UVA
Aslak Johansen, SDU
Bharathan Balaji, UCLA
Arka Bhattacharya, UC Berkeley
Gabriel Fierro, UC Berkeley

## Slide 13: Brick: Building Metadata Schema
Brick
Infrastructure: Sensors Equipment
Thermostat
HVAC
Lighting
Motion Sensor
Smoke Detector
Fire Safety
Management
Data Storage
Search
Privacy
Access Control
APIs
Monitoring
Applications
Occupant Interaction
Predictive Control
Fault Detection
NILM
Demand Response
Occupancy Models
Buildings
Office
Hospital
Shopping Mall
Factory
Home
Apartment

## Slide 14: Brick: Building Metadata Schema
Brick
Management
Data Storage
Search
Privacy
Access Control
APIs
Monitoring
Applications
Occupant Interaction
Predictive Control
Fault Detection
NILM
Demand Response
Occupancy Models
Completeness: Capture all sensors/subsystems
Expressiveness: Capture relationships to run applications
Usability: Easy to understand, easy to map buildings

## Slide 15: Outline
Why do we need Brick?
Brick
  Basics
  Development
  Results
Moving forward

## Slide 16: Outline
Why do we need Brick?
Brick
  Basics
  Development
  Results
Moving forward

## Slide 17: Brick is a Graph of Building Entities

## Slide 18: What Does Brick Contain?
CMU
IBM, Ireland
UCSD
Buildings
Tags, Tagsets
Class Hierarchy
Relationships
Brick

## Slide 19: An Example “Model” Building
AHU
Power Meter
Supply Fan
Lighting Controller
HVAC ZONE
VAV
Lighting Zone
Damper
Return Fan
Thermostat Temperature CO2 Sensor
Room 102
Room 101
Supply Air
Return Air

## Slide 20: Brick is a Graph of Building Entities
We choose to model this graph using ontologies
  Alternatives: Verilog, IFC
VAV
Room 1
Room 2
Temperature Sensor
AHU
Lighting
Controller
Lighting
Zone

## Slide 21: Tagsets: Brick Entities
Tagsets

## Slide 22: Tagsets and Tags
Tagsets: Building entities described in Brick
  “Zone Temperature Sensor”
  “Zone CO2 Sensor”
  “Room”
  “Air Handler Unit” (also called “AHU”)
Tags: Decomposition of tagsets
  “Zone Temperature Sensor” -> “Zone” “Temperature” “Sensor”
Tags facilitate annotation and keyword search
Tagsets facilitate semantic modeling
Thermostat Temperature CO2 Sensor

## Slide 23: Tagsets are Organized in a Hierarchy
Equipment
  Fire Safety System
  HVAC
    AHU
    Fan
      Supply Fan
    Thermostat
  …
Point
  Alarm
  Command
    Damper Command
  Sensor
    Temperature Sensor
  Setpoint
    Temperature Setpoint
  …
Location
  Building
  Room
    Conference Room
  HVAC Zone
  Lighting Zone
  …

## Slide 24: Relationships Link Tagsets
Essential to capture linkages between entities
Point
Location
Equipment
Legend
Class
Relationship
isPointOf, isPartOf
isPointOf, hasLocation
hasLocation
isPartOf, feeds
feeds
hasLocation

## Slide 25: Relationships in Example Building
Designed to capture essential aspects in BMS
Restrictions to avoid misuse: “hasLocation” limited to Location tagsets
Power Meter
Supply Fan
VAV
Damper
Return Fan
VAV
AHU
Damper
feeds
Power Meter
hasPoint
hasPart
AHU
HVAC Zone
feeds

## Slide 26: Relationships in Example Building
Temperature Sensor
VAV
Room 101
HVAC Zone
AHU
Damper
hasPoint
hasPoint
hasPart
feeds
feeds
Lighting Zone
Lighting Controller
Power Meter
Room 102
isLocationOf
controls
hasPoint
isLocationOf
isLocationOf
Location
Equipment
Point
Relationship
Legend

## Slide 27: Function Blocks
Enables modularity, encapsulation, reusability
Library of function blocks to ease development
VAV
Damper
VAV
Air Flow
Damper
controls
hasPoint
Damper Command
Damper Position
Zone Temperature
Temperature
Setpoint
Air Flow Setpoint
affects
controls
controls
AHU Supply Temperature
VAV
feeds

## Slide 28: Machine Readable & Queryable
Triples as data format
  subject predicate object
  Every entity is a URL brick: <http://buildsys.org/ontologies/Brick#>
  example:Berg_Hall rdf:type brick:Room example:Light hasLocation example:Berg_Hall
SPARQL for querying
  Pattern matches across the graph
  SELECT ?temp WHERE { ?temp rdf:type brick:Temperature_Sensor }

## Slide 29: Outline
Why do we need Brick?
Brick
  Basics
  Development
  Results
Moving forward

## Slide 30: Empirical Methodology
UC Berkeley
UVA
CMU
IBM, Ireland
UCSD
SDU
Six Buildings
Occupancy Modeling
Fault Detection
Participatory Feedback
NILM
Model Predictive Controls
Energy Apportionment
Demand Response
Web Displays
Eight Representative Applications
17700 points, 630000 sqft.

## Slide 31: Iterative Development Process
CMU
IBM, Ireland
UCSD
Buildings
Tags, Tagsets
Class Hierarchy
Relationships
Brick

## Slide 32: Iterative Development Process
Brick
SPARQL for Apps
CMU
IBM, Ireland
UCSD
Map Building Metadata
to Brick
Ground Truth Metadata
UC Berkeley
UVA
Coverage: 93.2%

## Slide 33: Outline
Why do we need Brick?
Brick
  Basics
  Development
  Results
Moving forward

## Slide 34: Coverage Across Buildings
Building | UCSD | CMU | IBM | UVA | Berkeley | SDU
Coverage | 96% | 99% | 99% | 98.5% | 98.7% | 98.8%

## Slide 35: App Query Matches for Buildings
 | UCSD | SDU | CMU | IBM | UVA | Berkeley
Occupancy |  |  |  |  |  | 
Energy Apportionment |  |  |  |  |  | 
Web Displays |  |  |  |  |  | 
MPC |  |  |  |  |  | 
Participatory Feedback |  |  |  |  |  | 
Fault Detection |  |  |  |  |  | 
NILM |  |  |  |  |  | 
Demand Response |  |  |  |  |  | 

## Slide 36: Live Demo

## Slide 37: Brick vs Haystack
AHU
HVAC
VAV
Temperature Sensor: TS
Floor
Room
Haystack
Brick
temp
point
vavRef
ahuRef
roomRef
sensor
floorRef
hvac
Id: TS
TS is a Temperature Sensor
TS hasLocation Room
TS isPointOf VAV

## Slide 38: Brick vs Haystack
 | Brick | Haystack

## Slide 39: Brick vs Haystack
 | Brick | Haystack
Reference Implementation | 6 buildings, 8 applications | None

## Slide 40: Brick vs Haystack
 | Brick | Haystack
Reference Implementation | 6 buildings, 8 applications | None
Relationships | Captures relationships within and across subsystems | Can link entities, but does not classify relationships

## Slide 41: Brick vs Haystack
 | Brick | Haystack
Reference Implementation | 6 buildings, 8 applications | None
Relationships | Captures relationships within and across subsystems | Can link entities, but does not classify relationships
Querying | SPARQL queries that traverse Brick graph | Restrictive query, cannot traverse relationships

## Slide 42: Brick vs Haystack
 | Brick | Haystack
Reference Implementation | 6 buildings, 8 applications | None
Relationships | Captures relationships within and across subsystems | Can link entities, but does not classify relationships
Querying | SPARQL queries that traverse Brick graph | Restrictive query, cannot traverse relationships
Encapsulation | Functional blocks encapsulate complex subsystems | No modularity

## Slide 43: Outline
Why do we need Brick?
Brick
  Basics
  Development
  Results
Moving forward

## Slide 44: Lessons Learned
Mapping buildings to Brick
  Semi-automated mapping: 5 papers in BuildSys 2015
New types of building and equipment
  Update building tagsets
  An unknown sensor can be referred to as “Sensor”
Separation of application from building infrastructure
  Application specific terms should not be part of Brick

## Slide 45: Moving Forward: Call to Action!
Open Sourced with BSD license
  http://brickschema.org/
Sustained improvements, extensions:
  Comments, issue tracking, pull requests on github
Integrate with building management systems
  We have an initial integration with BuildingDepot
Compatibility with IFC
  Exploit IFC “adapters” to convert CAD specs to Brick
Brick in Practice
  Usability testing, performance evaluation, tool-chain support

## Slide 46: Thank You!
Image credit: clipartpanda.com, school-pass.com, clker.com
http://brickschema.org/
Visit our Demo!
Jason Koh
Bharathan Balaji
Arka Bhattacharya
Gabriel Fierro
Authors who are at BuildSys
Yuvraj Agarwal
David Culler
Mikkel Kjaergaard
Mario Berges
Kamin Whitehouse